## Slide 1: Structural Fire Design for Buildings
Ahn, Jae-kwon
Korea Institute of Civil Engineering and Building Technology

## Slide 2
Introduction to Fire Safety
  Background
  Fire Safety
  Fire Resistance
  Current Issues
Fire and Heat
  Fuels & Fire Loads
  Fire Behavior & Heat Transfer
Structural Fire Design in Codes and Standards
  Methods of Assessing Fire Resistance
  Fire-resistance Requirements in Codes and Standards
  Prescriptive Method & Calculation Method in IBC
  Simple Calculation Method in EUROCODE
Advanced Structural Fire Design
  Background and Key Issues
  Performance-based Design Process
  Whole Building Behavior and the Use of Finite Element Models
Outline
Notes: To learn the behavior & design of structural components under fire exposure
To gain an educational & comprehensive experience in the fire resistance design concept
To learn basic fire safety design issues

## Slide 3
Background
  Building fires cause the loss of life and damage to property.
  Fire risk can be mitigated through conscientious design and maintenance.
    Actually, it is impossible to prevent all major building fires.
  Fire safety depends on numerous factors:
    Fire prevention, suppression and extinction
    Successful evacuation of occupants
    Structural integrity (or robustness)
Fires
  The Great Fire of London
    2nd September 1666, London, UK
    Within 5 days the city was destroyed by fire
    440 acres consumed, 87 churches, 13200 homes
  World Trade Center
    11th September 2001, New York, USA
    2,763 people deaths in the WTC
    Fire temperatures – about 1000° C
  Grenfell Tower fire
    14th June 2017, London, UK
    72 people deaths & 70 people injured
    Exterior cladding and insulation with combustible materials
Introduction to Fire Safety

## Slide 4
Role of Structures
  Various occupancy
    Building (commercial, industrial, residential), Outdoor stadium, Oil platform, Tower, Liquid storage tanks etc.
  Provide comfortable, safe, functional space
    Shelter and Support
    Withstands various types of loads - Dead, Live, Wind, Flood, Snow, Earthquake, Thermal, and Fire
Fire Safety
  Not possible to prevent all fire scenarios
  Designers need to put in-place strategies to minimize the occurrence of fires & consequently reducing their impact on life, property and environment.
  Main strategies include providing for:
    Automatic fire sprinklers - statistics show that sprinklers have a very high probability of controlling or extinguishing any fire
    Systems for fire detection and notification of fire service
    Safe travel paths for the movement of occupants & firefighters
    Barriers to control the spread of fire & smoke
    Fire resistant structures - not collapse prematurely in fire
  To strategize, the designer has the important responsibility to properly select, design and use building materials
Introduction to Fire Safety

## Slide 5
What is Fire Resistance?
  Fire resistance: “the property of a material or assemblage to withstand fire or give protection from it.
  Provide physical barrier to restrict fire spread
    prevent fire and smoke spread
    safe evacuation of occupants & firefighter
    minimize life loss and injury
  Maintain structural integrity and load carrying ability against fire
    Minimize property damage
    prevent structural collapse
    Compartmentation & Structural integrity are principal aspects of fire safety in buildings
    Fire Resistance Rating – Codes
  The importance of fire resistance depends on the size of the building & the fire safety objectives that need to be satisfied.
Introduction to Fire Safety

## Slide 6
Issue 1 - Performance-based design codes
  Current approach to fire safety design: Prescriptive based approach
    Significant drawbacks
  Many countries including US and Europe are moving towards performance-based codes
    Rational engineering approaches
    Offers cost-effective, innovative & alternate designs
  Performance-based design approach needs:
    Validated models, test data for validation, material properties
    Design tools/guidelines, trained personnel, monitoring tools
Issue 2 – New materials (High performance material)
  High Strength Concrete, Fiberglass Reinforced Plastic
    Benefits: Superior performance(Strength, Durability, Corrosion resistance…)
    Applications: Bridges, Infrastructure projects(Retrofitting & strengthening)
  High Performance Material - Plastics, Composites
    Benefits: Superior strength, Light weight
    Applications: Auto, Aerospace, Transportation
  Major problem in fire performance
    High temperature intolerant
    Toxicity
    Flame spread (combustible)
    Faster strength/stiffness degradation
Introduction to Fire Safety

## Slide 7
Fuels – Materials
  Material available as fuel are part of the building structure, lining materials, or contents of the building
    All materials are hydrocarbons, their molecules consisting mainly of carbon & atoms, with the addition of oxygen, nitrogen & others in some cases
Fuels – Calorific Value
  Heat release rates (HRR) from combustion depend on the nature of the burning material, the size of the fire, and the amount of air available.
  The calorific value or heat of combustion is the amount of heat released during complete combustion of a unit mass of fuel.
    Most solid, liquid and gaseous fuels have a calorific value between 15 and 50 MJ/kg
    Net calorific values of combustible materials for calculation of fire loads in EUROCODE 1
Fire and Heat
Combustible materials |  | MJ/kg
Solid | Wood | 17.5
 | Clothes, Cork, Cotton, Paper, cardboard, Silk, Straw, Wool | 20
 | Carbon: Anthracit, Charcoal, Coal | 30
Chemicals | Methane, Ethane, Propane, Butane | 50
 | Ethylene, Propylen, Butene | 45
 | Benzene, Toluene | 40
 | Methanol, Ethanol, Ethyl alcohol | 30
 | Gasoline, petroleum Diesel, Pure hydrocarbons | 45
 | Polyethylene, Polystyrene, Polypropylene | 40

## Slide 8
Fire Load
  Fire load in buildings is usually expressed as Fire Load Energy Density per floor area(MJ/m2).
    Note that some references express fire load as energy density per total room bounding surfaces.
Design Fire Load
  should be determined in a similar way to design loads
    Earthquake load vs. Extreme likely design fire scenario
  should reflect almost the maximum fire load expected in building life
  Both fixed and moveable fire loads should be included.
  Fire load densities qf,k [MJ/m²] for different occupancies in EUROCODE 1
Fire and Heat
Occupancy | Average (MJ/kg) | 80% Fractile (MJ/kg)
Dwelling | 780 | 948
Hospital | 230 | 280
Hotel | 310 | 377
Library | 1500 | 1824
Office | 420 | 511
Classroom of a school | 285 | 347
Shopping centre | 600 | 730
Theatre (cinema) | 300 | 365
Transport (public space) | 100 | 122

## Slide 9
Heat Release Rate & t-squared Fires
  Heat release rate (HRR)
    The HRR (MW) can be calculated by the amount of heat (MJ) released in a certain time (s).
    Q = E/t
      E is the total energy contained in the fuel (MJ)
      t is the duration of the burning (s)
  t-squared fires
    characterized by a parabolic curve with the HRR proportional to the time squared
    Q = (t/k)2 = ( t)2
      Q is the HRR (MW), t is the time (s),
      k is the growth constant (s/MW1/2), and  is the fire intensity coefficient (MW/s2)
Fire and Heat
Fire Growth Rate | Growth Constant | Fire Intensity Coefficient | Typical Real Fire
Slow | 600 | 0.00293 | Densely packed wood products
Medium | 300 | 0.0117 | Solid wood furniture such as desk Individual furniture items with small amount of plastic
Fast | 150 | 0.0466 | Some upholstered furniture High stacked wood pallets Cartons on pallets
Ultra-fast | 75 | 0.1874 | Most upholstered furniture High stacked plastic materials Thin wood furniture such as wardrobs

## Slide 10
Heat Release Rate & t-squared Fires
  Variation of HRR (same fire load): slow, medium and fast fire growth rates
  Combination of t-squared HRRs for separately & combined for two objects
Fire and Heat

## Slide 11
Fire Behavior in Building Compartment
  The factors influencing the severity of a fire in a compartment are:
    fire load type, density and distribution
    combustion behavior of the fire load
    compartment size and geometry
    ventilation conditions of the compartment
    thermal properties of the compartment boundary
  Stages of an enclosed compartment fire
    Growth phase(pre-flashover)
    Flashover
    Fully developed phase (post-flashover)
    Decay phase
    Extinction
  Options for modelling compartment fires
    Nominal fire
    Time equivalence
    Natural fire curves
    Localized fires
    Zone models
    CFD/field models
Fire and Heat

## Slide 12
Heat Transfer - Conduction
  Conduction is the mechanism for heat transfer in solid materials
    factor in the ignition of solid surfaces, & in the fire resistance of barriers & structural members
    Thermal properties needed for heat transfer calculations in solid materials include:
      density,  (kg/m3), specific heat, Cp (J/kg-K), thermal conductivity, k (W/m-K)
      thermal diffusivity,  = k/Cp (m2/s), thermal inertia, kCp (W2s/m4K2)
Fire and Heat
Fire condition | convection coefficient (W/m2K)
Standard fires | 25
External fires | 25
Hydrocarbon fires | 50
Parametric fires | 35
Unexposed side (without & with radiation) | 4 & 9
Material | Emissivity
Carbon steel | 0.7
Stainless steel | 0.4
Concrete | 0.7
Others | 0.8
Heat Transfer - Convection
  Convection is heat transfer by the movement of fluids, either gases or liquids
    Heat transfer by convection is an important factor in flame spread and in upward transport of smoke and hot gases to the ceiling or out of the window from a room fire
    Convective heat transfer is usually taken to be directly proportional to the temp difference between 2 materials
Heat Transfer - Radiation
  Radiation is the transfer of energy by waves
  Very important in fires because it is the main mechanism for heat transfer from:
    flames to fuel surfaces
    hot smoke to building objects
    a burning building to an adjacent building

## Slide 13
Methods of Assessing Fire Resistance
  The fundamental step in designing structures for fire safety is to verify that the fire resistance of the structure is greater than the severity of the fire to which the structure is exposed.
  Fire resistance  Fire severity
    Fire resistance is a measure of the ability of the structure to resist collapse or fire spread during exposure to a fire of specified severity.
    Fire severity is a measure of the destructive impact of a fire, or the forces or temp. that may cause collapse or fire spread as a result of a fire.
  Methods for comparing fire severity with fire resistance
    The most common verification is comparing fire severity and fire resistance in time domain.
    Temperature domain is more suitable for barriers than structural elements.
    Load capacity in a fire can be calculated using thermal & structural analyses at high temperature.
    Prescriptive codes specify required fire resistance which is generally between half an hour and four hours, but with no reference to the severity of the expected fire
    Performance-based codes allow the use of time equivalent formulae to improve on simple prescriptive fire-resistance requirements
Structural Fire Design in Codes and Standards
Domain | Fire Resistance | Fire severity
Time | Time to failure | Fire duration as calculated or specified by codes
Temperature | Temperature to cause failure | Maximum temperature reached during the fire
Strength | Load capacity at elevated temperature | Applied load during the fire

## Slide 14
Fire-resistance Requirements in Codes and Standards
  Building codes set fire-resistance requirements for building assemblies to resist
    Spread of fire within buildings
    Collapse of structural elements exposed to fire
  Construction type & Occupancy
    Construction type
      Type I & II - Non-combustible : Concrete, Masonry, Steel
      Type III - Non-combustible exterior walls & Combustible/Non-combustible interior elements
      Type IV - Non-combustible exterior walls & Interior elements of solid wood, laminated wood, heavy timber (HT)
      Type V - allows the use of all types of materials, both noncombustible and combustible.
    Occupancy
      Assembly
      Business
      Educational
      Factory & Industrial
      High Hazard
      Institutional
      Mercantile
      Residential
      Storage
      Utility/Miscellaneous
Structural Fire Design in Codes and Standards

## Slide 15
Fire-resistance Requirements in Codes and Standards
  Maximum allowable height & area of a building are determined based on
    Construction type & Occupancy
Structural Fire Design in Codes and Standards

## Slide 16
Fire-resistance Requirements in Codes and Standards
  Fire-resistance rating requirements for building elements in IBC (hours)
Structural Fire Design in Codes and Standards
Building element | TYPE Ⅰ |  | TYPE Ⅱ |  | TYPE Ⅲ |  | TYPE Ⅳ | TYPE Ⅳ | 
 | A | B | A | B | A | B | HT | A | B
Primary structural frame | 3 | 2 | 1 | 0 | 1 | 0 | HT | 1 | 0
Exterior bearing walls | 3 | 2 | 1 | 0 | 2 | 2 | 2 | 1 | 0
Interior bearing walls | 3 | 2 | 1 | 0 | 1 | 0 | 1/HT | 1 | 0
Floor | 2 | 2 | 1 | 0 | 1 | 0 | HT | 1 | 0
Roof | 1½ | 1 | 1 | 0 | 1 | 0 | HT | 1 | 0
  Construction types in NFPA 220 (Standard on types of building construction)
    3 Digit Code: e.g. 332.
    1st digit: fire resistance of exterior bearing wall
    2nd digit: fire resistance of columns, beams, girders, trusses and arches
    3rd digit: fire resistance of floor construction

## Slide 17
Traditional Approaches to Structural Fire Design
  Standard fire test
    Most countries assess fire performance of building materials & elements using full-size fire resistance tests
    Refer to results from standard test; no “engineering analysis” required
    More than 100 years
    ASTM E119, NFPA 251, UL 263, ISO 834, BS 476
Structural Fire Design in Codes and Standards

## Slide 18
Traditional Approaches to Structural Fire Design
  Code-based prescriptive design
    Most codes have been prescriptive in nature for fire resistance evaluation.
    Code-based prescriptive design may restrict designers to take a rational engineering approach to the provisions of fire safety
  Minimum protection of structural parts based on time periods for various noncombustible insulating materials
Structural Fire Design in Codes and Standards
Structural parts | Insulating material | Minimum thickness for required fire resistance time (inches) |  |  | 
 |  | 4 hours | 3 hours | 2 hours | 1 hour
Steel columns and all of primary trusses | Carbonate, lightweight and sand-lightweight aggregate concrete, members 6”×6” or greater | 2.5 | 2 | 1.5 | 1
 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 8”×8” or greater | 2 | 1.5 | 1 | 1
 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 12”×12” or greater | 1.5 | 1 | 1 | 1
 | Siliceous aggregate concrete, members 6”×6” or greater | 3 | 2 | 1.5 | 1
 | Siliceous aggregate concrete, members 8”×8” or greater | 2.5 | 2 | 1 | 1
 | Siliceous aggregate concrete, members 12”×12” or greater | 2 | 1 | 1 | 1
Webs or flanges of steel beams and girders | Carbonate, lightweight and sand-lightweight aggregate concrete with 3” or finer metal mesh placed 1” from the finished surface anchored to the top flange and providing no less than 0.025 square inch of steel area per foot in each direction | 2 | 1.5 | 1 | 1
 | Siliceous aggregate concrete and concrete excluded in Item 2-1.1 with 3" or finer metal mesh placed 1" from the finished surface anchored to the top flange and providing not less than 0.025 square inch of steel area per foot in each direction. | 2.5 | 2 | 1.5 | 1

## Slide 19
IBC - Calculation Method for Fire Resistance of Structures
  includes the methods to calculate the fire-resistance rating for an assembly (concrete, concrete-masonry, clay masonry, steel and wood).
Structural Fire Design in Codes and Standards

## Slide 20
IBC - Calculation Method for Fire Resistance of Structures
  also contains provisions that would permit modifications or changes to a tested assembly.
Structural Fire Design in Codes and Standards

## Slide 21
Structural Design in Fire Conditions
  In concept, structural design for fire exposed to fire
    similar to structural design for room temperature conditions
    must establish clear objectives & determine design fire severity
    Working stress or ultimate strength design may be carried out
  Main differences between fire & ambient design are:
    applied loads are less
    internal forces may be induced by thermal expansion
    strength of materials may be reduced by elevated temp.
    cross-sectional areas may be reduced, i.e., charring
    smaller safety factors used
    deflections with no effect on strength are not important
    different failure mechanisms need to be considered
  Tools available to predict structural fire resistance of a load-bearing members include:
    Hand calculations
    Design charts
    Computer programs
Structural Fire Design in Codes and Standards

## Slide 22
Thermal and mechanical properties of materials
  Thermal properties
    Thermal elongation
    Specific heat
    Thermal conductivity
    Density
  Mechanical properties
    Stress-strain relationship: Effective yield strength, Slope of the linear elastic range, Proportional limit
Structural Fire Design in Codes and Standards

## Slide 23
Simple calculation method in EUROCODE
  Eurocode 2: Design of concrete structures - Part 1-2: General rules - Structural fire design
    Two simplified methods using a reduced cross-section
    applicable to structures subjected to a standard fire exposure
    500°C isothermal method
      concrete at a temperature more than 500°C is neglected in the calculation of load-bearing capacity
      concrete at a temperature below 500 °C is assumed to retain its full strength.
    Zone method
      the fire damaged cross-section is reduced by ignoring a damaged zone at the fire-exposed surfaces.
Structural Fire Design in Codes and Standards

## Slide 24
Simple calculation method in EUROCODE
  Eurocode 3: Design of steel structures - Part 1-2: General rules - Structural fire design
    Simplified methods modifying the design resistance for normal temperature design
    usually used the hypothesis of a uniform temperature in the cross-section
  Eurocode 4: Design of composite steel and concrete structures - Part 1-2: General rules - Structural fire design
    Simplified methods considering composite effects of steel and concrete
    Detailed procedure of simple calculation for composite column
Structural Fire Design in Codes and Standards

## Slide 25
Performance-based design
  Disadvantages of prescriptive approach
    Actual structural behavior & Real fire effect are ignored.
    Levels-of-safety and robustness are unknown.
    Optimum solution for life safety, economical impact and environmental damage are unknown.
  Many countries are moving towards performance-based codes which
    Sate how a building is to perform under a wide range of conditions
    Use of calculation/engineering methods
    Allow actual behavior and robustness of the building to be assessed
    Allow designers to use alternate fire safety strategies, provided adequate safety can be demonstrated
    Allow optimum design solution taking into account life safety, financial impact and environmental issues
    can be used to justify cost-effective solutions
    Can be used as part of an assessment of multiple risks
  Within a prescriptive code, there may be possibility to allow for performance-based selection of structural assemblies
    if a code specifies a floor with a fire resistance rating, designers have the flexibility to select from a range of listed systems which have sufficient fire resistance
  However, Standard calculation methods have not yet been developed for widespread use
Advanced Structural Fire Design

## Slide 26
Performance-based design
  In developing new codes, many countries have adopted a multi-level code format in the form of:
    overall goals, functional objectives and required performance which must be achieved
    selection of alternative means of achieving those goals. The three most common options are:
      to comply with a prescriptive 'Acceptable Solution'
      to comply with an approved standard calculation method
      to perform a performance-based fire engineering design from first principles
  So, compliance with performance-based codes is usually achieved by:
    Mainly satisfying the requirements of acceptable solutions, or
    Carrying out a performance-based alternative design based on fire engineering principles
  Under a performance-based design, it is essential to have comprehensive documentation & quality control
    The calculations should be included in a report which describes the building & the complete fire design process
Advanced Structural Fire Design

## Slide 27
Performance-based design process
Advanced Structural Fire Design
Three components of structural fire engineering design

## Slide 28
Assessment methods for thermal exposure
Advanced Structural Fire Design
Assessment Method | Model for thermal Exposure | Description
Level 1 | H1 | Standard fire exposure – test or tabulated data
Level 2 | H2 | Equivalent fire duration time – relates the severity of a compartment fire to an equivalent period in a standard furnace
Level 3 | H3 | Parametric exposure – uses physical characteristics of the fire compartment as input parameters
Level 4 | H4 | Advanced methods – zone or field models used to characterize the full compartment response for the required duration

## Slide 29
Options for estimating the heat transfer
Advanced Structural Fire Design
Model | Design charts/test data | Simple formulae | Advanced models
Complexity | Simple | Intermediate | Advanced
Analysis ability | Exact solution Standard fire condition | Empirical solution Standard fire condition | Accurate solution Any fire condition
Member types | Dependent on available test data | Mainly steel members | Any material and construction methods
Input parameters | Construction type & Member geometry | Heat flux or fire curves, Boundary conditions, Member geometry, Material thermal properties | 
Solutions | Cross-sectional temperature charts Tabulated thermal data | Simple cross-sectional temperature profile | One to three-dimensional time and space dependent temperature profile
Design tools | Fire part of Eurocodes Test/Research reports | Fire part of Eurocodes Design guides | Finite element package
 | Design charts/tables | Spreadsheet | Computer models

## Slide 30
Options for Structural Analysis
Advanced Structural Fire Design
Model | Design charts/test data | Simple formulae | Advanced models
Complexity | Simple | Intermediate | Advanced
Input parameters | Temperature through the cross-section Material strength and stiffness reduction Applied static load Simplified boundary conditions | Temperature through the cross-section and along the member Material strength and stiffness reduction Applied static load Boundary conditions | Temperature through and along the cross- section Full material stress-strain- temperature relationship Applied static load Boundary conditions Element type and density
accuracy | Ignores real behaviour but assumed to be conservative Ultimate strength calculation | Begins to consider actual load paths and restraint Ultimate strength calculation | Predicts internal stresses, displacements, and rotations for all members throughout the duration of the fire Localized behavior is not modelled accurately in whole building modelling
design tools | Simple equations for hand calculations | Simple equations for hand calculations Plastic design, redistribution of moments Simple computer models | Commercially available or purpose written computer software

## Slide 31
Whole building behavior and the use of advanced models
  Purpose-written or commercially available finite element software can be used to assess the structural response under fire conditions
  Structural fire engineers should be adequately experienced to identify the assumptions and approximations embedded within the software including its limitations.
Advanced Structural Fire Design

## Slide 32
Structural Fire Engineering
  Fire is one of the severe disasters that cause a great loss of life and property.
  Purkiss (2007) :
    “The application of scientific and engineering principles to the effects of fire in order to reduce the loss of life and damage to property by quantifying the risks and hazards involved and provide an optional solution to the application of preventive or protective measure.”
Structural Fire Design in Codes and Standards
  Assessment methods of fire resistance in time, temperature, and strength domains
  Fire-resistance rating requirements for building elements based on construction type and occupancy
  Reviewed the prescriptive method and calculation method in IBC
  Also reviewed the simple calculation method in EUROCODE 2/3/4
Advanced Structural Fire Design
  Drawbacks of the current design method based on the prescriptive approach
  Process of performance-based structural fire design
  Reviewed the options for heat transfer and structural analysis
  Possibility of structural assembly and whole building behavior analysis using advanced models
Summary

## Slide 33
Codes & Standards
  ACI 216.M-07, Standard Method for Determining Fire Resistance of Concrete and Masonry Construction Assemblies
  AISC 360-16, Specification for Structural Steel Building
  ASCE/SFPE 29-05, Standard Calculation Methods for Structural Fire Protection
  Eurocode 1, Actions on Structures, Part 1.2: General Actions - Actions on Structures Exposed to Fire
  Eurocode 2, Design of Concrete Structures, Part 1.2: General Rules-Structural Fire Design
  Eurocode 3, Design of Steel Structures, Part 1.2: General Rules-Structural Fire Design
  Eurocode 4, Design of Composite Steel and Concrete Structures, Part 1.2: General Rules-Structural Fire Design
  International Building Code
  ISO 834-1: Fire Resistance Test–Elements of Building Construction
  NFPA 5000, Building Construction and Safety Code
Books
  Andrew H. Buchanan, Structural Design for Fire Safety
  IStrucE, Guide to the advanced fire safety engineering of structures
  SFPE Handbook of Fire Protection Engineering
  Y.C. Wang, Steel and Composite Structures: Behavior and Design for Fire Safety
References